## Register Table
Register Address | Contents (hex) | Contents (dec) | Description | Beschreibung | Read/Write | Datablocks | Data type / response | LCD page | Modbus | Modbus Register Type | Function Code | Remarks | Select
1000 | 4000 | 16384 | Serial number | Seriennummer | Read | 4 | signed | P62 | R | input | 04 | By default last 8 digits of serial number
1010 | 4002 | 16386 | Meter code | Zählercode | Read | 2 | signed | / | R | input | 04 | 0102 DC version; 0103 CT version
1018 | 4003 | 16387 | Meter ID (iBus/Modbus) | Zähler-ID (iBus/Modbus) | Read/write | 2 | HEX response | P61 | R/W | holding | 03 | 001-247 (001 default)
1020 | 4004 | 16388 | Baud Rate | Baud-Rate | Read/write | 2 | HEX response | P64 | R/W | holding | 03 | 9600 (default), 4800, 2400, 1200, 600, 300
1050 | 4005 | 16389 | Protocol Version | Protokollversion | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 | 3.2 = New Modbus protocol
1054 | 4007 | 16391 | Software Version | Softwareversion | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 | Shows present software version
1058 | 4009 | 16393 | Hardware Version | Hardware-Version | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 | 1.03, will be updated if hardware modifications are made
1060 | 400B | 16395 | Meter Amps | Amperemeter | Read | 4 | HEX response | / | R | input | 04 | 100 for DC version; 5 for CT version
1062 | 400C | 16396 | CT rate | CT-Rate | Read/write | 2 | signed | P58 | R/W | holding | 03 | 5:0-50:0; 75:0; 125:0; 200:0; 250:0; 300:0; 400:0; 500:0; 800:0; 1000:0; 1500:0; 2000:0; 2500:0; 3000:0; 4000:0; 5000:0; 7500:0
1066 | 400D | 16397 | S0 output rate | S0-Ausgangsrate | Read/write | 2 | Float - Big Endian (ABCD) | P59 / P60 | R/W | holding | 03 | 1000, 2000, 10000, 20000, 40000
107A | 400F | 16399 | Combined Code | Kombinierter Code | Read/write | 2 | HEX response | P60 | R/W | holding | 03 | 01 (A), 05 (06, 09 and 10)
1510 | 4010 | 16400 | LCD cycle time | LCD-Zykluszeit | Read/write | 2 | signed | P63 | R/W | holding | 03 | 0-30 (seconds, 10 seconds default)
1520 | 4011 | 16401 | Parity setting | Paritätseinstellung | Read/write | 2 | signed | / | R/W | holding | 03 | 01 (even); 02 (none)
2000 | 5000 | 20480 | Voltage | Spannung | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 | Only for 1 phase meter (PRO1 series)
2008 | 5002 | 20482 | L1 Voltage | Spannung L1 | Read | 4 | Float - Big Endian (ABCD) | P38 | R | input | 04 |  | x
200C | 5004 | 20484 | L2 Voltage | Spannung L2 | Read | 4 | Float - Big Endian (ABCD) | P39 | R | input | 04 |  | x
2010 | 5006 | 20486 | L3 Voltage | Spannung L3 | Read | 4 | Float - Big Endian (ABCD) | P40 | R | input | 04 |  | x
2020 | 5008 | 20488 | Grid frequency | Netzfrequenz | Read | 4 | Float - Big Endian (ABCD) | P56 | R | input | 04 |  | x
2060 | 500A | 20490 | Current | Strom | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 | Only for 1 phase meter (PRO1 series)
2068 | 500C | 20492 | L1 Current | Strom L1 | Read | 4 | Float - Big Endian (ABCD) | P41 | R | input | 04 |  | x
206C | 500E | 20494 | L2 Current | Strom L2 | Read | 4 | Float - Big Endian (ABCD) | P42 | R | input | 04 |  | x
2070 | 5010 | 20496 | L3 Current | Strom L3 | Read | 4 | Float - Big Endian (ABCD) | P43 | R | input | 04 |  | x
2080 | 5012 | 20498 | Total Active Power | Gesamt-Wirkleistung | Read | 4 | Float - Big Endian (ABCD) | P44 | R | input | 04 |  | x
2088 | 5014 | 20500 | L1 Active Power | Wirkleistung L1 | Read | 4 | Float - Big Endian (ABCD) | P45 | R | input | 04
208C | 5016 | 20502 | L2 Active Power | Wirkleistung L2 | Read | 4 | Float - Big Endian (ABCD) | P46 | R | input | 04
2090 | 5018 | 20504 | L3 Active Power | Wirkleistung L3 | Read | 4 | Float - Big Endian (ABCD) | P47 | R | input | 04
20A0 | 501A | 20506 | Total Reactive Power | Gesamt-Blindleistung | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04 |  | x
20A8 | 501C | 20508 | L1 Reactive Power | Blindleistung L1 | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04
20AC | 501E | 20510 | L2 Reactive Power | Blindleistung L2 | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04
20B0 | 5020 | 20512 | L3 Reactive Power | Blindleistung L3 | Read | 4 | Float - Big Endian (ABCD) | / | R | input | 04
20C0 | 5022 | 20514 | Total Apparent Power | Gesamt-Scheinleistung | Read | 4 | Float - Big Endian (ABCD) | P48 | R | input | 04 |  | x
20C8 | 5024 | 20516 | L1 Apparent Power | Scheinleistung L1 | Read | 4 | Float - Big Endian (ABCD) | P49 | R | input | 04
20CC | 5026 | 20518 | L2 Apparent Power | Scheinleistung L2 | Read | 4 | Float - Big Endian (ABCD) | P50 | R | input | 04
20D0 | 5028 | 20520 | L3 Apparent Power | Scheinleistung L3 | Read | 4 | Float - Big Endian (ABCD) | P51 | R | input | 04
20E0 | 502A | 20522 | Power Factor | Leistungsfaktor | Read | 4 | Float - Big Endian (ABCD) | P52 | R | input | 04 |  | x
20E8 | 502C | 20524 | L1 Power Factor | Leistungsfaktor L1 | Read | 4 | Float - Big Endian (ABCD) | P53 | R | input | 04
20EC | 502E | 20526 | L2 Power Factor | Leistungsfaktor L2 | Read | 4 | Float - Big Endian (ABCD) | P54 | R | input | 04
20F0 | 5030 | 20528 | L3 Power Factor | Leistungsfaktor L3 | Read | 4 | Float - Big Endian (ABCD) | P55 | R | input | 04
2200 | 6048 | 24648 | Tariff | Tarif | Read/write | 2 | signed | / | R/W | holding | 03 | 01 (1h saved), 02 (2h saved)
3000 | 6000 | 24576 | Total Active Energy | Gesamt-Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P02 | R | input | 04 |  | x
3100 | 6002 | 24578 | T1 Total Active Energy | T1 Gesamt-Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P03 | R | input | 04
3200 | 6004 | 24580 | T2 Total Active Energy | T2 Gesamt-Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P04 | R | input | 04
3008 | 6006 | 24582 | L1 Total Active Energy | Wirkenergie L1 | Read | 4 | Float - Big Endian (ABCD) | P11 | R | input | 04
300C | 6008 | 24584 | L2 Total Active Energy | Wirkenergie L2 | Read | 4 | Float - Big Endian (ABCD) | P14 | R | input | 04
3010 | 600A | 24586 | L3 Total Active Energy | Wirkenergie L3 | Read | 4 | Float - Big Endian (ABCD) | P17 | R | input | 04
3020 | 600C | 24588 | Forward Active Energy | Wirkenergie-Bezug | Read | 4 | Float - Big Endian (ABCD) | P05 | R | input | 04 |  | x
3120 | 600E | 24590 | T1 Forward Active Energy | T1 Wirkenergie-Bezug | Read | 4 | Float - Big Endian (ABCD) | P06 | R | input | 04
3220 | 6010 | 24592 | T2 Forward Active Energy | T2 Wirkenergie-Bezug | Read | 4 | Float - Big Endian (ABCD) | P07 | R | input | 04
3028 | 6012 | 24594 | L1 Forward Active Energy | Wirkenergie-Bezug L1 | Read | 4 | Float - Big Endian (ABCD) | P12 | R | input | 04
302C | 6014 | 24596 | L2 Forward Active Energy | Wirkenergie-Bezug L2 | Read | 4 | Float - Big Endian (ABCD) | P15 | R | input | 04
3030 | 6016 | 24598 | L3 Forward Active Energy | Wirkenergie-Bezug L3 | Read | 4 | Float - Big Endian (ABCD) | P18 | R | input | 04
3040 | 6018 | 24600 | Reverse Active Energy | Eingespeiste Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P08 | R | input | 04 |  | x
3140 | 601A | 24602 | T1 Reverse Active Energy | T1 Eingespeiste Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P09 | R | input | 04
3240 | 601C | 24604 | T2 Reverse Active Energy | T2 Eingespeiste Wirkenergie | Read | 4 | Float - Big Endian (ABCD) | P10 | R | input | 04
3048 | 601E | 24606 | L1 Reverse Active Energy | Eingespeiste Wirkenergie L1 | Read | 4 | Float - Big Endian (ABCD) | P13 | R | input | 04
304C | 6020 | 24608 | L2 Reverse Active Energy | Eingespeiste Wirkenergie L2 | Read | 4 | Float - Big Endian (ABCD) | P16 | R | input | 04
3050 | 6022 | 24610 | L3 Reverse Active Energy | Eingespeiste Wirkenergie L3 | Read | 4 | Float - Big Endian (ABCD) | P19 | R | input | 04
3060 | 6024 | 24612 | Total Reactive Energy | Gesamt-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P20 | R | input | 04 |  | x
3160 | 6026 | 24614 | T1 Total Reactive Energy | T1 Gesamt-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P21 | R | input | 04
3260 | 6028 | 24616 | T2 Total Reactive Energy | T2 Gesamt-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P22 | R | input | 04
3068 | 602A | 24618 | L1 Total Reactive Energy | Blindenergie L1 | Read | 4 | Float - Big Endian (ABCD) | P29 | R | input | 04
306C | 602C | 24620 | L2 Total Reactive Energy | Blindenergie L2 | Read | 4 | Float - Big Endian (ABCD) | P32 | R | input | 04
3070 | 602E | 24622 | L3 Total Reactive Energy | Blindenergie L3 | Read | 4 | Float - Big Endian (ABCD) | P35 | R | input | 04
3080 | 6030 | 24624 | Forward Reactive Energy | Vorwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P23 | R | input | 04 |  | x
3180 | 6032 | 24626 | T1 Forward Reactive Energy | T1 Vorwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P24 | R | input | 04
3280 | 6034 | 24628 | T2 Forward Reactive Energy | T2 Vorwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P25 | R | input | 04
3088 | 6036 | 24630 | L1 Forward Reactive Energy | Vorwärts-Blindenergie L1 | Read | 4 | Float - Big Endian (ABCD) | P30 | R | input | 04
308C | 6038 | 24632 | L2 Forward Reactive Energy | Vorwärts-Blindenergie L2 | Read | 4 | Float - Big Endian (ABCD) | P33 | R | input | 04
3090 | 603A | 24634 | L3 Forward Reactive Energy | Vorwärts-Blindenergie L3 | Read | 4 | Float - Big Endian (ABCD) | P36 | R | input | 04
30A0 | 603C | 24636 | Reverse Reactive Energy | Rückwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P26 | R | input | 04 |  | x
31A0 | 603E | 24638 | T1 Reverse Reactive Energy | T1 Rückwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P27 | R | input | 04
32A0 | 6040 | 24640 | T2 Reverse Reactive Energy | T2 Rückwärts-Blindenergie | Read | 4 | Float - Big Endian (ABCD) | P28 | R | input | 04
30A8 | 6042 | 24642 | L1 Reverse Reactive Energy | Rückwärts-Blindenergie L1 | Read | 4 | Float - Big Endian (ABCD) | P31 | R | input | 04
30AC | 6044 | 24644 | L2 Reverse Reactive Energy | Rückwärts-Blindenergie L2 | Read | 4 | Float - Big Endian (ABCD) | P34 | R | input | 04
30B0 | 6046 | 24646 | L3 Reverse Reactive Energy | Rückwärts-Blindenergie L3 | Read | 4 | Float - Big Endian (ABCD) | P37 | R | input | 04

## Notes
T1, T2 | Tariff-Values; only applicable if you have configured a standard and alternative tariff